PASS / RESUBMIT

City of Escondido

Fire Department

1163 N Centre City Parkway

Escondido, CA 92026

Phone: 760-839-5400 Fax: 760-739-7060

FIRE PLAN CHECK FORM/CORRECTION

List for Commercial Land Industrial Occupancies

Date ____________ City Plan Check Number:                                      County Plan Check #____________

Project Name:                                                       			Address:

Corrections circled are to be made on the plans before Fire Approval will be issued.  The approval of plans and specifications does not permit the violation of any section of the Fire Department Fire Code, County Ordinances, or State law.  The following list does not necessarily include all errors and omissions.

To facilitate rechecking, please identify, next to each circled item, the sheet of the plans upon which the correction has been made. RETURN THIS CORRECTION LIST WITH THE CORRECTED PLANS Note: If new plans are provided when resubmitting, return at least one copy of the original stamped and checked set.

## A.	PLAN REQUIREMENTS

- Due to the number and/or complexity of corrections, before Fire sign-off will be given, corrections should be made on the originals and run new prints.

- Identify rooms and specify use.

- Define all symbols and shaded areas etc. used on the plans.

- See notes/remarks made on one set of plans.  Return marked set with new/revised sets after you have complied with the requirements on the marked set of plans.  Red marks on plans are part of this comments list.

- The Fire Department will require the following conditions be placed on the project: Detailed information regarding Fire District Ordinances can be found on the District’s web site at: http://fire.escondido.org, under fire prevention.

B.	SITE REQUIREMENTS

______ 1. SITE INSPECTION may reveal conditions which have changed since plan review.  When such discrepancies                 arise, field inspection shall take precedence.

______ 2. SHOW FIRE HYDRANT LOCATIONS (Note on plot plan) (Sec. 507): Minimum hydrant spacing for commercial projects is every 350 unless otherwise noted per Appendix C.

______ 3. FIRE DEPARTMENT CONNECTIONS: Shall be located within 40 feet of the nearest hydrant and have signage to                 identify the structures that FDC serves and not attached to the structure.

______ 4.  GATES (503.6) (Note on plot plan): No person shall install a security gate or security device across a fire access roadway without the fire code official's approval. All gates providing access from a road to a driveway shall be located a minimum of 30 feet from the nearest edge of the roadway and the driveway width shall be 36 feet wide at the entrance on roadways of 24 feet or less of the traffic lane(s) serving the gate. An automatic gate across a fire access roadway or driveway shall be equipped with an approved emergency key-operated switch overriding all command functions and opening the gate. A gate accessing more than four residences or residential lots or a gate accessing hazardous institutional, educational or assembly occupancy group structure, shall also be equipped with an approved emergency traffic control-activating strobe light sensor or other device approved by the fire code official, which will activate the gate on the approach of emergency apparatus with a battery back-up or manual mechanical disconnect in case of power failure.

______ 5. KEY BOXES & SWITCHES (506.1) (Note on plot plan): When access to or within a structure or an area is unduly difficult because of secured openings or where immediate access is necessary for life saving or firefighting purposes, the  Fire code official is authorized to require a key box to be installed in an accessible location.  The key box shall be a type approved by the fire code official and shall contain keys to gain necessary access as required by the fire code official.

______ 6. EMERGENCY KEY ACCESS (506.2.1): All central station-monitored fire detection systems and fire sprinkler systems shall have an approved emergency key access box on site in an approved location.  The owner or occupant shall provide and maintain current keys for the structure(s) for fire department placement in the box, and shall notify the fire department in writing when the building is re-keyed.

______ 7. THE ANGLE OF DEPARTURE AND ANGLE OF APPROACH (503.2.7): The angle of departure and angle of approach of a fire access roadway shall not exceed 7 degrees (12 percent) or as approved by the fire code official.

______ 8. TURNING RADIUS (503.2.4): The turning radius of a fire apparatus access road shall comply with the City/County public and private road standards.  The turning radius for a private residential driveway shall be a minimum of 28 feet, as measured on the inside edge of the improvement width or as approved by the fire code official.

______ 9. GRADE (503.2.7) (Show on plot plan): The gradient for a fire apparatus access roadway shall not exceed 20.0%.  Grades exceeding 15.0% shall not be allowed without mitigation measures. The fire code official may require additional mitigation measures where he deems appropriate. The standard cross-slope shall be 2 percent; minimum cross-slope shall be 1 percent; maximum cross-slope shall be 5 percent.

______ 10. SURFACE (503.2.3) (Note on plot plan): Fire apparatus access roads shall be designed and maintained to support the imposed loads of fire apparatus not less than 75,000 lbs. unless authorized by the FAHJ and shall be provided with an approved paved surface so as to provide all-weather driving capabilities.

______ 11. STREET NUMBERS (505.1) (Note on plot plan): Approved numbers and/or addresses shall be placed on all new and existing buildings and at appropriate additional locations as to be plainly visible and legible from the street or roadway fronting the property from either direction of approach.  Said numbers shall contrast with their background, and shall meet the following minimum standards as to size: 4" high with a 1/2” stroke for residential buildings, 6" high with a ½" stroke for commercial and multi-residential buildings, 12" high with a 1" stroke for industrial buildings.  Additional numbers shall be required where deemed necessary by the Fire Marshal, such as rear access doors, building corners, and entrances to commercial centers.  The Fire code official may establish different minimum sizes for numbers for various categories of projects.

______ 12. ELEVATORS:  Elevators shall be capable of accommodating a Fire Department gurney. Show dimensions on plans.

______ 13. FIRE APPARATUS ACCESS (503)

Plans for fire apparatus access roads or for their modification shall be submitted to the fire department for review and approval prior to construction or modification.

______ 14. MAP DIRECTORIES (505.4)

A lighted directory map, meeting current fire department standards, shall be installed at each driveway entrance to multiple unit residential projects and mobile home parks, where the numbers of units in such projects exceed 15.

______ 15. ROADWAY DESIGN FEATURES (503.4.1): Roadway design features (speed bumps, speed humps, speed control dips, etc.) which may interfere with emergency apparatus responses shall not be installed on fire access roadways, unless they meet design criteria approved by the fire code official.

______ 16. FIRE LANE DESIGNATION & MARKING (§ 503.3-503.3.1) (Note on plot plan): Where required by the fire code official, approved signs or other approved notices shall be provided for fire apparatus access roads to identify such roads or prohibit the obstruction thereof. Where the fire code official determines that it is necessary to ensure adequate fire access, the fire code official may designate existing roadways as fire access roadways as provided by Vehicle Code section 22500.1 (public) or 22658(a) (private).

______ 17. ADDITIONAL ACCESS (503.1.2): The fire code official is authorized to require more than one fire apparatus access road based on the potential for impairment of a single road by vehicle congestion, condition of terrain, climatic conditions or other factors that could limit access.

______ 18. ACCESS ROADS WITHIN 150 FT OF BUILDINGS (503.1.1): Access roads shall be provided within 150 feet of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route.

______ 19. EMERGENCY RESPONDER RADIO COVERAGE (510 & 510.4.1): Buildings shall have minimum radio signal strength of -95 dBm in 95% of all areas on each floor of the building. Coverage shall comply with section 510 of the CFC.

______ 20. RESPONSE MAP UPDATES (505.5): Any new development, which necessitated updating of emergency response maps by virtue of new structures, hydrants, roadways, or similar features, shall be required to provide map updates in a format (PDF or approved by FAHJ) or compatible with current department mapping services.

______ 21. COMBUSTIBLES ON SITE (Note on plot plan):  An adequate water supply and approved paved all-weather suface must be installed prior to any combustibles on site.

C.	MECHANICAL AND ELECTRICAL REQUIREMENTS

______ 1. LOCATION OF LPG TANK, ABOVE GROUND STORAGE: Minimum separation between containers and buildings public ways, or lines of adjoining property that can be built upon is: 10 feet for containers 125 gallons to 500 gallons 25 feet for containers 501 to 2,000 gallons.

______ 2. DUCT DETECTORS: Provide the remote test stations on the floor plans for all duct detectors.

## D.	ROOFING REQUIREMENTS

______ 1. ROOFING (4905.4) (Note on plot plan): Class “A” Very High Fire Hazard Areas

  - Roof gutters –Prevent debris accumulation

  - Replacement – more than 50% or more 2,500 square feet roof area

______ 2. VENT REQUIREMENTS (4905.4): Prevent intrusion of flame and embers into the attic.

______ 3. STAIRWAY ACCESS TO ROOF (504.3): Buildings over 4 stories in height shall provide stair way access to the                   roof.

## E.	GENERATOR INSTALLATION

______ 1. CONTAINMENT: Provide secondary containment for the generator fuel storage tank. Show on plans.

______ 2. VEHICLE DAMAGE PREVENTION: Bollards shall be installed to prevent vehicle damage to the generator fuel                   tank. Show on plans.

F. FIRE PROTECTION SYSTEMS

______ 1. DEFERRED SUBMITTALS (Note on plot plan): All Fire protection plans including, but not limited to, Fire Sprinkler, Fire Alarm, and Fire Underground lines, shall be a deferred submittal to the Escondido Fire Department regardless of the scope of work. Plans must be submittal and approved by Escondido Fire Department prior to any work being done.

______ 2. UNDERGROUND FIRE LINE PLANS (Note on plot plan): Engineering/ grading/ improvement plans shall not be submitted in lieu of a deferred underground fire line plan. Underground fire lines shall be installed per NFPA 24.

______ 2. FIRE SPRINKLERS (902.1) (Note on plot plan): Structures shall meet National Fire Protection Association Standards 13, 13-D and 13-R latest addition, and Escondido Fire Department installation policies as appropriate.

______ 3. AUTOMATIC FIRE SPRINKLER SYSTEMS (903.2): Approved automatic Fire sprinkler systems are required in all new structures. For the purpose of fire-sprinkler systems, buildings separated by less than ten (10) feet from adjacent buildings shall be considered as one building.  Fire barriers, partitions and walls, regardless of rating, shall not be considered as creating separate buildings for purposes of determining fire sprinkler requirements.  Mezzanines shall be included in the total square footage calculation.

______ 4. AUTOMATIC FIRE SPRINKLER SYSTEM- REMODELS OR RECONSTRUCTION (903.2.8.2): An automatic sprinkler system installed in accordance section 903.2 may be required if the scope of work includes significant modification to the interior or roof of the building, and the cost of installation of an automatic sprinkler system does not exceed 15 percent of the construction costs of the remodel. When Fire Sprinklers are required under remodels and reconstructions this shall mean the entire structure or structures shall be equipped with fire sprinklers. The fire code official may require that other protective measures be taken based on existing conditions and/or potential hazards.

______ 5. SPRINKLER SYSTEM MONITORING AND ALARMS: Automatic sprinkler systems with 20 or more sprinkler heads shall be monitored.

______ 6. FIRE ALARMS/SMOKE DETECTORS (907)

  - Fire Alarms and smoke detectors shall be installed and maintained in accordance with Fire Code Section  907 and NFPA 72

  - Central Station monitoring is required for all commercial occupancies.

______ 7.  FIRE EXTINGHISHING SYSTEMS

- Fire extinguishers shall be provided and maintained every 3,000 square feet and maximum 75 feet travel distance.  Extinguishers shall have a minimum rating per occupancy classification. Identify location and size of extinguishers on floor plan.

- Class K extinguishers shall be installed within 30 feet of commercial food heat processing stations

- Hood and Duct Systems required to have a Type I hood shall be protected with an approved automatic fire-extinguishing system.

- Commercial Cooking Systems must be in Compliance with UL 300 and CFC.

F. MID-RISE BUILDINGS

______ 1. Mid-Rise Buildings Sec 319.1 General:  All newly constructed mid-rise buildings or any mid-rise building which undergoes a complete renovation that requires the complete vacancy of the building to complete the renovation shall comply with this section.

Exceptions:

- Buildings used exclusively as an open parking garage.

- Buildings where all floors above the fourth floor level are used exclusively as an open parking garage.

- Buildings such as a power plant, lookout tower, steeple, grain house, and other similar structures with non-continuous human occupancy

G. EXITING

- All occupancies shall have an adequate number of exits.

- Exit Doors shall swing in the direction of travel when the occupant load exceeds 49.

- Exit paths shall be illuminated when the building is occupied.

- When the exit path is not easily identifiable, additional signs may be required.

- Provide occupant load, occupant load factor, and exit analysis

- Provide dead end and travel distance limits

- Doors shall be readily operable from the egress side without the use of a key or special knowledge or          	   effort

8	  Second floor with occupant load over 10 requires 2 exits with one leading directly outside

9      Identify the maximum travel distance.

H.	  ADDITIONAL REQUIREMENTS, additional sheet(s) may be attached.

Plan Checker:                        			Phone Number _______________________	Date: